## Appendix-Parshall
Appendix-A 5-9
Calculating Size of Approach Channel for Parshall Plume
|  | choice 1 |  | choice 2 |  | choice 3
Lower value of flow in MLD | Enter | 45 | Enter | 45 | Enter | 45
Higher value of flowin MLD | Enter | 170 | Enter | 170 | Enter | 170
Lower value of flow in lps | C4*1000000/24/3600 | 520.8333 | E4*1000000/24/3600 | 520.8333 | G4*1000000/24/3600 | 520.8333
Higher value of flow in lps | C5*1000000/24/3600 | 1967.5926 | E5*1000000/24/3600 | 1967.5926 | G5*1000000/24/3600 | 1967.5926
Throat width (W) in m, from Table | Enter | 0.3 | Enter | 0.6 | Enter | 0.9
Mouth width (D)in m,from Table | Enter | 0.83 | Enter | 1.12 | Enter | 1.55
Liquid depth in m at low flow | POWER((C6/2264/C8),(1/1.5)) | 0.83779 | POWER((E6/2264/E8),(1/1.5)) | 0.52777 | POWER((G6/2264/G8),(1/1.5)) | 0.40277
Liquid depth in m at high flow | POWER((C7/2264/C8),(1/1.5)) | 2.0322 | POWER((E7/2264/E8),(1/1.5)) | 1.2802 | POWER((G7/2264/G8),(1/1.5)) | 0.97696
velocity at mouth in low flow in m/s | C4*1000/24/3600/C9/C10 | 0.74901 | E4*1000/24/3600/E9/C10 | 0.88112 | G4*1000/24/3600/G9/G10 | 0.83428
velocity at mouth in high flow in m/s | C5*1000/24/3600/C9/C11 | 1.1665 | E5*1000/24/3600/E9/C11 | 1.3723 | G5*1000/24/3600/G9/G11 | 1.2993
Approach channel width, m | C9 | 0.83 | E9 | 1.12 | G9 | 1.55
Approach channel, liquid depth, m | C11 | 2.0322 | E11 | 1.2802 | G11 | 0.97696
Summary of Options |  | Choice 1 |  | Choice 2 |  | Choice 3
Width of approach channel , m | C14 | 0.83 | E14 | 1.12 | G14 | 1.55
Liquid depth in approach channel, m | C11 | 2.0322 | E11 | 1.2802 | G11 | 0.97696
Width of throat, m | C8 | 0.3 | E8 | 0.6 | G8 | 0.9
It may be seen that the velocities at low flow are met adequately in all three chosen widths. However, the ease of O&M has
also to be considered. Choice 1 gives a very narrow width and very deep channel. This will be difficult to maintain. Between choice 2
and choice 3, both can be used. However, choice 2 will give almost a square section and lesser width for easy maintanance