## Appendix-5-12
Appendix-A 5-12 - Illustrative Design of conventional ASP aeration
Leave 3 blank rows at the top and start from cell A4. Copy column A in your excel, Then copy column C in your excel, Then enter each cell of column C by prefixing = sign in column B
Then enter your inputs in column B, Then copy column B and paste in column D, Then enter the winter temparature in cell D6
Plant design flow, MLD | 50 | Enter | 50
Elevation of site above MSL, m | 30 | Enter | 30
Operating temparature in deg C | 30 | Enter | 20
Primary clarifier effluent BOD, mg/l | 230 | Enter | 230
Thickener overflow return as fraction of plant flow | 0.15 | Enter | 0.15
Thickener overflow return, MLD | 7.5 | B4*B8 | 7.5
Thickener overflow return BOD, mg/l | 500 | Enter | 500
Centrate from sludge dewatering as fraction of plant flow | 0.006 | Enter | 0.006
Centrate from sludge dewatering return, MLD | 0.3 | B4*B11 | 0.3
Centrate from sludge dewatering return BOD, mg/l | 380 | Enter | 380
Influent BOD to aeration tank, mg/l | 265.8131 | ((B4*B7)+(B9*B10)+(B12*B13))/(B4+B9+B12) | 265.8131
Effluent BOD | 20 | Enter | 20
Weighted BOD to be removed in the aeration tank, mg/l | 245.8131 | B14-B15 | 245.8131
MLSS | 3000 | Enter | 3000
F : M | 0.35 | Enter | 0.35
F | 14208 | B16*(B4+B9+B12) | 14208
| 40594.2857 | B19/B18 | 40594.2857
Aeration tank volume calculated from F/M, cum | 13531.4286 | (B20/B17)*1000 | 13531.4286
Mean Cell Residence Time, Theta C, days | 3 | From Fig 5-38 | 5
Constant Y | 0.5 | Fixed value | 0.5
constant Kd | 0.06 | Fixed value | 0.06
Aeration tank volume calculated from Theta, cum | 5207.9057 | B23*B4*1000*B16*B22/(1+B24*B22)/B17 | 7878.6266
HRT for average flow as per CPHEEO, hrs | 5 | 4 to 6 in Table 5-9 | 5
Aeration tank volume calculated from HRT, cum | 10416.6667 | B4*1000*B26/24 | 10416.6667
Maximum of the three volumes of aeration tank, cum | 13531.4286 | Max(B21,B25,B27,D21,D25,D27) | 13531.4286
liquid depth, m (restrict to max of 6.5 m if air cooled) | 5.5 | Enter | 5.5
BOD removed in aeration tank, kg/day | 14208 | (B4+B9+B12)*B16 | 14208
Kg oxygen / Kg of BOD removed | 0.9 | 0.8 to 1.0 in Table 5-9 | 0.9
Kg of Oxygen needed per day | 12787.2 | B30*B31 | 12787.2
Residual D. O. in aeration | 2 | Fixed value | 2
If surface aerators are used
Alpha value | 0.83 | Enter by Designer-See also clause 5.8.1.7.5.3 | 0.83
Beta value | 0.95 | As in clause 5.8.1.7.5.3 | 0.95
D O at operating temparature | 7.43 | 14.42+(0.003*B6*B6)-(0.323*B6) | 9.16
D O at operating elevation | 7.4051 | (1-(B5/152)*0.017)*B38 | 9.1293
Oxygen tension, mg/l | 5.0348 | (B39*B37)-B33 | 6.6728
Oxygen gradient, mg/l | 0.54905 | B40/9.17 | 0.72768
Temparature difference | 10 | B6-20 | 0
Temparature Co-efficient | 1.03 | Fixed Value | 1.03
Temparature correction factor | 1.3439 | Power(B43,B42) | 1
Conversion factor to standard conditions | 0.61244 | B41*B36*B44 | 0.60397
Oxygen needed under standard conditions, kg / day | 20879.052 | B32/B45 | 21171.8316
Provide factor of safety for intangibles | 1.1 |  | 1.1
Oxygen needed after factor of safety , kg/day | 22966.9572 | B46*B47 | 23289.0147
Oxygen transfer capacity of aerator Kg/Kwhr | 1.8 | 1.2 to 2.4 in clause 5.8.1.7.5.3 | 1.8
Kw of aerator needed | 531.6425 | B48/24/B49 | 539.0976
If diffused aeration is used
Factor for temperature power 3 | 0.027 | POWER(B6,3)/(POWER(10,6)) | 0.008
Factor for temperature power 2 | 0.0012857 | (POWER(B6,2)/(POWER(10,5))/7) | 0.00057143
Factor for temperature power 1 | 0.09 | 0.003*B6 | 0.06
Density of air at operating temparature | 1.2207 | 1.285+B53-B54-B55 | 1.2324
Content of oxygen in air | 0.232 | Fixed value | 0.232
Kg of oxygen needed for residual D O per day | 100 | B4*B33 | 100
Total kg of oxygen needed per day | 12887.2 | B32+B58 | 12887.2
Air needed in cum / day | 45504.7315 | B59/B56/B57 | 45072.2071
Transfer efficiency of diffuser system per m depth (*) | 0.05 | Fixed | 0.05
Transfer efficiency at design depth | 0.275 | B29*B61 | 0.275
diffuser fouling factor per year | 0.04 | Enter | 0.04
Diffuser life cycle, years | 3 |  | 3
Diffuser fouling factor for its life cycle | 1.1249 | POWER((1+B63),B64) | 1.1249
Provide factor of safety for intangibles | 1.1 | B47 | 1.1
Air needed for oxygenetation in cum / day | 204746.5374 | B60*B65*B66/B62 | 163898.9351
Air needed for oxygenetation in cum / hour | 8531.1057 | B67/24 | 6829.1223
Air mixing criteria cum /minute / 1000 cum of tank | 16 | As in clause 5.8.1.7.5.6 | 16
Air needed for mixing as per manual cum / hr | 12990.1714 | B28*B69*60/1000 | 12990.1714
Air needed for mixing as per manual in cum / hr | 2.7 | 1.8 to 2.7 as per US EPA, 625/8-85/0100, p 38 | 2.7
Surface area of aeration tank, sqm | 2460.2597 | B28/B29 | 2460.2597
Air needed for mixing as per US EPA guidelines in cum / hr | 6642.7013 | B71*B72 | 6642.7013
Maximum of air needed for mixing in cum / hr | 12990.1714 | MAX(B70:B73) | 12990.1714
Air needed as higher of oxygenation and mixing cum / hr | 12990.1714 | MAX(B68,B74) | 12990.1714
Air needed as under standard conditions, cum / hr | 21210.4655 | B75/B45 | 21507.8924
Friction and other losses as fraction of depth | 0.2 | Enter by Designer | 0.2
Liquid depth as water column for air pressure | 6.6 | B29*(1+B77) | 6.6
Kw of needed compressor at 1400 rpm | 486.6262 | 0.746*((0.03*B76)+16) | 493.2826
For DPR purpose, equation for Compressor Kw at 1400 rpm for 7 m water column can be taken as BHP = 0.03*(cum / hr)+16
For DPR purpose, equation for Compressor Kw at 1400 rpm for 6 m water column can be taken as BHP = 0.025*(cum / hr)+13
For DPR purpose, equation for Compressor Kw at 1400 rpm for 5 m water column can be taken as BHP = 0.02*(cum / hr)+14
Sludge Flows
Y0bs=Y/(1+Kd*ThetaC) | 0.42373 | (B23)/(1+B24*B22) | 0.38462
Excess Sludge mass wasted Kg/day | 5207.9057 | B84*B16*B4 | 4727.1759
Kgd of excess sludge / Kg of BOD removed | 0.4 | 0.35 to 0.5 as per clause 5.8.1.7.5.10 | 0.4
Kg of excess sludge from thumb rule per day | 4916.263 | B4*B16*B86 | 4916.263
Excess sludge as higher of the two values, Kg/ day | 5207.9057 | MAX(B85,B87, D85, D87) | 5207.9057
Concentration factor for MLSS in return / excess sludge | 3.3 | Enter by Designer | 3.3
Return / excess sludge MLSS concentration, mg/l | 9900 | B17*B89 | 9900
Cells in aeration, kg | 40594.2857 | B17*B28/1000 | 40594.2857
Cells wasting from system kg / day | 5207.9057 | B88 | 5207.9057
Volume of excess sludge, cum / day | 526.0511 | B92*1000000/B90/1000 | 526.0511
Resulting Theta C | 7.7947 | B91/B92 | 7.7947
Least Theta C in design | 3 | MIN(B22,D22) | 5
Volume of excess sludge for least Theta C | 1366.811 | B93*B94/B95 | 820.0866
Excess sludge pump set duty as cum / day | 1366.811 | MAX(B93,B96,D93,D96) | 1366.811
Recirculation ratio | 0.8 | 0.25 to 0.8 as per Table 5.9 | 0.8
Return sludge pumpset duty as MLD | 40 | B4*B98 | 40
Motors of both the return sludge and excess sludge pump sets will be provided with VFD to downsize actual pumpage as needed