## Appendix-4-1
1 | B | C | D
2 | Appendix A 4-1
3 | Friction factor for Fittings in Pressure Mains
4 | Given the type and numbers of fittings, find the total friction factor
5 | This is left blank for the designer to enter his design notes
6 | Number of Sudden contractions | Enter by Designer | 2
7 | Friction Factor for each | From Table 4.2 | 0.5
8 | Friction factor for all | D6*D7 | 1
9 | Entrance shape well rounded | Enter by Designer | 1
10 | Friction Factor for each | From Table 4.2 | 0.5
11 | Friction factor for all | D9*D10 | 0.5
12 | Elbow 90 degrees | Enter by Designer | 4
13 | Friction Factor for each | From Table 4.2 | 1
14 | Friction factor for all | D12*D13 | 4
15 | Elbow 45 degrees | Enter by Designer | 4
16 | Friction Factor for each | From Table 4.2 | 0.75
17 | Friction factor for all | D15*D16 | 3
18 | Elbow 22 degrees | Enter by Designer | 2
19 | Friction Factor for each | From Table 4.2 | 0.5
20 | Friction factor for all | D18*D19 | 1
21 | Tee 90 degrees | Enter by Designer | 4
22 | Friction Factor for each | From Table 4.2 | 1.5
23 | Friction factor for all | D21*D22 | 6
24 | Tee in straight pipe | Enter by Designer | 1
25 | Friction Factor for each | From Table 4.2 | 0.3
26 | Friction factor for all | D24*D25 | 0.3
27 | Gate valve open | Enter by Designer | 4
28 | Friction Factor for each | From Table 4.2 | 0.4
29 | Friction factor for all | D27*D28 | 1.6
30 | Valve with reducer and increaser | Enter by Designer | 3
31 | Friction Factor for each | From Table 4.2 | 0.5
32 | Friction factor for all | D30*D31 | 1.5
33 | Globe valve | Enter by Designer | 4
34 | Friction Factor for each | From Table 4.2 | 10
35 | Friction factor for all | D33*D34 | 40
36 | Angle | Enter by Designer | 2
37 | Friction Factor for each | From Table 4.2 | 5
38 | Friction factor for all | D36*D37 | 10
39 | Swing check | Enter by Designer | 1
40 | Friction Factor for each | From Table 4.2 | 2.5
41 | Friction factor for all | D39*D40 | 2.5
42 | Venturi meter | Enter by Designer | 1
43 | Friction Factor for each | From Table 4.2 | 0.3
44 | Friction factor for all | D42*D43 | 0.3
45 | Orifice | Enter by Designer | 1
46 | Friction Factor for each | From Table 4.2 | 1
47 | Friction factor for all | D45*D46 | 1
48 | Total friction factor | D8+D11+D14+D17+D20+D23+D26+D29+D32+D35+D38+D41+D44+D47 | 72.7

## Appendix-4-4
1 | Appendix A 4-4
2 | B | C | D | E | F | G | H | I | J | K | L
3 | Appendix A 4-4 B: Condition of flow; Appendix A 4-4 D: Immediate flows; Appendix A 4-4 G: Intermediate flows; Appendix A 4-4 J: Ultimate flows
4 | Stage |  | low | ave | peak | low | ave | peak | low | ave | peak
5 | Appendix A 4-4 B: Average flow, cum / day; Appendix A 4-4 C: Enter by Designer; Appendix A 4-4 E: 1500; Appendix A 4-4 H: 3800; Appendix A 4-4 K: 7900
6 | Proportion | Enter by Designer | 0.6 | 1 | 2.2 | 0.6 | 1 | 2.2 | 0.6 | 1 | 2.2
7 | Design flow, cum / day | E5*D6, E5*E6, E5*F6 | 900 | 1500 | 3300 | 2280 | 3800 | 8360 | 4740 | 7900 | 17380
8 | Hazen Williams C | Enter by Designer | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
9 | Desired velocity, m/s | 0.8, D9*E6/D6, D9*F6/D6 | 0.8 | 1.3333 | 2.9333 | 0.8 | 1.3333 | 2.9333 | 0.8 | 1.3333 | 2.9333
10 | Area needed, sqm | D7/24/3600/D9 | 0.013021 | 0.013021 | 0.013021 | 0.032986 | 0.032986 | 0.032986 | 0.068576 | 0.068576 | 0.068576
11 | Dia needed, m | SQRT(D10*4/3.14) | 0.12879 | 0.12879 | 0.12879 | 0.20499 | 0.20499 | 0.20499 | 0.29556 | 0.29556 | 0.29556
12 | Dia needed, mm | D11*1000 | 128.7907 | 128.7907 | 128.7907 | 204.9891 | 204.9891 | 204.9891 | 295.5646 | 295.5646 | 295.5646
13 | Radius, m | D11/2 | 0.064395 | 0.064395 | 0.064395 | 0.10249 | 0.10249 | 0.10249 | 0.14778 | 0.14778 | 0.14778
14 | Radius power 0.63 | POWER(D13,0.63) | 0.17766 | 0.17766 | 0.17766 | 0.23809 | 0.23809 | 0.23809 | 0.29982 | 0.29982 | 0.29982
15 | S power 0.54 | D9/0.848/D8/D14 | 0.053103 | 0.088504 | 0.19471 | 0.039623 | 0.066039 | 0.14529 | 0.031465 | 0.052442 | 0.11537
16 | S | POWER(D15,(1/0.54)) | 0.0043562 | 0.011218 | 0.048311 | 0.0025329 | 0.006523 | 0.028091 | 0.0016528 | 0.0042564 | 0.01833
17 | Slope 1 in | 1/D16 | 229.5603 | 89.1386 | 20.699 | 394.8062 | 153.3038 | 35.5989 | 605.0519 | 234.9425 | 54.5564
18 | length, m | Enter by Designer | 960 | 960 | 960 | 960 | 960 | 960 | 960 | 960 | 960
19 | Friction in pipeline, m | D18/D17 | 4.1819 | 10.7697 | 46.379 | 2.4316 | 6.2621 | 26.9671 | 1.5866 | 4.0861 | 17.5965
20 | Velocity head, m | D9*D9/2/9.81 | 0.03262 | 0.09061 | 0.43855 | 0.03262 | 0.09061 | 0.43855 | 0.03262 | 0.09061 | 0.43855
21 | Frction factor in fittings | 'Appendix-4-1'!C47 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7
22 | Friction in fittings, m | D20*D21 | 2.3715 | 6.5874 | 31.8829 | 2.3715 | 6.5874 | 31.8829 | 2.3715 | 6.5874 | 31.8829
23 | Static lift, m | Enter by designer | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5
24 | Total head, m | D22+D23 | 28.8715 | 33.0874 | 58.3829 | 28.8715 | 33.0874 | 58.3829 | 28.8715 | 33.0874 | 58.3829
25 | Efficiency of pumpset | Enter by designer | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
26 | Discharge, lps | D7*1000/24/3600 | 10.4167 | 17.3611 | 38.1944 | 26.3889 | 43.9815 | 96.7593 | 54.8611 | 91.4352 | 201.1574
27 | Kw required | D26*D24/D25/100.5 | 3.7406 | 7.1447 | 27.7351 | 9.4762 | 18.0999 | 70.2623 | 19.7005 | 37.6287 | 146.0716
28 | Appendix A 4-4 B: Option 1
29 | Appendix A 4-4 B: Provide 150 mm pipeline at zero year and another 150 mm at 11th year and another 250 mm in 21st year and change pumpsets at 11th and 21st years
30 | Appendix A 4-4 B: The augmnentation at 21st year can be decided based on realistic conditions at that time. May be suitable for smaller systems
31 | Appendix A 4-4 B: Option 2
32 | Appendix A 4-4 B: Provide 200 mm pipeline at zero year and provide pump sets also as for the 11th year flowrate and use the storage volume in the wet well and sewer system
33 | Appendix A 4-4 B: The augmnentation at 21st year can be decided based on realistic conditions at that time. May be suitable for very large systems
34 | Appendix A 4-4 B: Basis for Decision
35 | Appendix A 4-4 B: Unlike water pumping, sewage varies widely and grit adds to the problem
36 | Appendix A 4-4 B: Hence, paramount importance is to ensure minimum of 0.8 m/s all times.
37 | Appendix A 4-4 B: Each system to be weighed carefully based on calculations for that system