## Appendix-A5-10
Appendix-A5-10
Illustrative Sizing of Clarifiers
Primary Clarifiers followed by secondary treatment
Average flow, MLD | Enter | 25
Peak flow. MLD | Enter | 65
Overflow rate for average flow from Table 5.8. m3/m2/day | Enter | 35
Overflow rate for peak flow from Table 5.8, m3/m2/day | Enter | 80
Surface area for average flow, sqm | C4*1000/C6 | 714.2857
Surface area for peak flow, sqm | C5*1000/C7 | 812.5
Higher of the two areas, sqm | MAX(C8,C9) | 812.5
Required diamter, m | SQRT(4*C10/3.14) | 32.1719
Resulting weir length, m | 3.14*C10 | 101.0198
Resulting weirloading rate, m3/m /day | C3*1000/C11 | 247.4762
Weir loading rate in average flow from Table 5.8, m3/m /day | Enter | 125
Usage of double sided weir is needed or not | Enter | Yes
Choose a launder clear annular space from inner sidewall of clarifier, m | Enter | 0.2
Choose a launder width, m | Enter | 0.6
Diameter of outer weir, m | C10-C15-C15 | 31.7719
Diameter of inner weir, m | C17-C16-C16 | 30.5719
Total length of weir, m | 3.14*(C17+C18) | 195.7596
Resulting weir loading rate, m3/m /day | C3*1000/C19 | 127.7077
Weir loading is safe or not | Enter | Yes
Side water depth shall be to suit Table 5.8
In actual practice, the diamter and the size of launder will be not less than the above values
Secondary Clarifiers for activated sludge
Average flow, MLD | Enter | 25
Peak flow. MLD | Enter | 65
Return sludge flow, MLD | Enter | 12
MLSS, mg/L | Enter | 3500
Overflow rate for average flow from Table 5.8. m3/m2/day | Enter | 25
Overflow rate for peak flow from Table 5.8, m3/m2/day | Enter | 40
Surface area for average flow for overflow rate, sqm | C26*1000/C30 | 1000
Surface area for peak flow for overflow rate, sqm | C27*1000/C31 | 1625
Solids loading for average flow from Table 5.8. kg/m2/day | Enter | 100
Solids loading for peak flow from Table 5.8, kg/m2/day | Enter | 210
Surface area for average flow for solids loading, sqm | (C26+C28)*C29/C34 | 1295
Surface area for peak flow for solids loading, sqm | (C27+C28)*C29/C35 | 1283.3333
Higher of the four areas, sqm | MAX(C32,C33,C36,C37) | 1625
Required diamter, m | SQRT(4*C38/3.14) | 45.498
Resulting weir length, m | 3.14*C39 | 142.8636
Resulting weirloading rate at average flow, m3/m /day | (C26)*1000/C40 | 174.9921
Weir loading rate in average flow from Table 5.8, m3/m /day | Enter | 185
Usage of double sided weir is needed or not | Enter | No
Choose a launder clear annular space from inner sidewall of clarifier, m | Enter | 0.2
Side water depth shall be to suit Table 5.8
In actual practice, the diamter and side water depths will be not less than the above values
Depending on the area and diameter, multiple number of these clarifiers may be designed