## Appendix-A6-3
Appendix A6.3
Calculation of Friction Losses in Sludge Pipelines
for Gravity conditions and pumped conditions
For Gravity Conditions
Pipe material considered is UPVC
value of Manning's n | Enter from Table 3.11 | 0.01
Discharge rate m3/day | Enter by Designer | 500
Discharge rate in liters per second | C7*1000/24/3600 | 5.787
Required velocity, m/sec | Enter by Designer | 1.2
Required area in sqcm | (C8/C9/1000)*100*100 | 48.2253
diameter in mm | 10*SQRT(4*C10/3.14) | 78.3795
Hydraulic mean radius R in m | C11/4/1000 | 0.019595
diameter in mm power 0.67 | POWER(C11,0.67) | 18.583
Gradient power 0.5 | C9*C6*1000/3.968/C13 | 0.16274
Gradient | C14*C14 | 0.026484
Length of pipeline, m | Enter by Designer | 100
Friction loss, m | C15*C16 | 2.6484
Solids content of sludge in percent | Enter by Designer | 4
Friction compounding factor | 2.88+(0.176*C18*C18)-0.866*C18 | 2.232
Total friction head, m | C17*C19 | 5.9113
Add safety factor at percent | Enter by Designer | 10
Design friction head, m | C20*(1+(C21/100)) | 6.5024
For Pumped Conditions of raw sludge
Pipe material considered is UPVC
Solids in sludge as percent | Enter by Designer | 4
Value of Hazen C | Enter from Table 6.5 | 53
Discharge in cum / day | Enter by Designer | 75
Discharge rate in liters per second | C28*1000/24/3600 | 0.86806
Required velocity, m/sec | Enter by Designer | 1.5
Required area in sqcm | (C29/1000/C31)*100*100 | 5.787
diameter in mm | 10*(SQRT(4*C31/3.14)) | 27.1515
diameter in mm power 0.67 | POWER(C32,0.67) | 9.1336
Gradient power 0.54 | C30*1000/4.567/C27/C32 | 0.67849
Gradient | POWER(C34,(1/0.54)) | 0.48758
Length of pipeline, m | Enter by designer | 15
Friction loss, m | C35*C36 | 7.3136
Friction compounding factor | Enter from Figure 6.2 | 3
Total friction head, m | C37*C38 | 21.9409
Add safety factor at percent | Enter by Designer | 10
Design friction head, m | C39*(1+(C30/100)) | 22.27
Number of tees | Enter by designer | 2
Friction factor for tee |  | 1.5
Number of valves | Enter by designer | 2
Friction factor for valve |  | 1.4
Total friction co-efficient | (C42*C43)+(C44*C45) | 5.8
velocity head, m | C30*C30/2/9.81 | 0.11468
Friction loss in bends & tees | C46*C47 | 0.66514
Other Losses, m | Enter by designer | 0.33257
Total friction loss, m | C41+C48+C49 | 23.2677