## Appendix-A5-11
Appendix-A5-11
Illustrative Sizing of Clarifiers
Primary Clarifiers followed by secondary treatment
Average flow, MLD | Enter | 23
Peak flow. MLD | Enter | 60
Overflow rate for average flow from Table 5.8. m3/m2/day | Enter | 35
Overflow rate for peak flow from Table 5.8, m3/m2/day | Enter | 80
Surface area for average flow, sqm | C4*1000/C6 | 657.1429
Surface area for peak flow, sqm | C5*1000/C7 | 750
Higher of the two areas, sqm | MAX(C8,C9) | 750
Required diamter, m | SQRT(4*C10/3.14) | 30.9098
Resulting weir length, m | 3.14*C10 | 97.0567
Resulting weirloading rate, m3/m /day | C3*1000/C11 | 236.9749
Weir loading rate in average flow from Table 5.8, m3/m /day | Enter | 125
Usage of double sided weir is needed or not | Enter | Yes
Choose a launder clear annular space from inner sidewall of clarifier, m | Enter | 0.2
Choose a launder width, m | Enter | 0.6
Diameter of outer weir, m | C10-C15-C15 | 30.5098
Diameter of inner weir, m | C17-C16-C16 | 29.3098
Total length of weir, m | 3.14*(C17+C18) | 187.8334
Resulting weir loading rate, m3/m /day | C3*1000/C19 | 122.449
Weir loading is safe or not | Enter | Yes
Side water depth shall be to suit Table 5.8
In actual practice, the diamter and the size of launder will be not less than the above values
Secondary Clarifiers for activated sludge
Average flow, MLD | Enter | 23
Peak flow. MLD | Enter | 60
Return sludge flow, MLD | Enter | 12
MLSS, mg/L | Enter | 3500
Overflow rate for average flow from Table 5.8. m3/m2/day | Enter | 25
Overflow rate for peak flow from Table 5.8, m3/m2/day | Enter | 40
Surface area for average flow for overflow rate, sqm | C26*1000/C30 | 920
Surface area for peak flow for overflow rate, sqm | C27*1000/C31 | 1500
Solids loading for average flow from Table 5.8. kg/m2/day | Enter | 100
Solids loading for peak flow from Table 5.8, kg/m2/day | Enter | 210
Surface area for average flow for solids loading, sqm | (C26+C28)*C29/C34 | 1225
Surface area for peak flow for solids loading, sqm | (C27+C28)*C29/C35 | 1200
Higher of the four areas, sqm | MAX(C32,C33,C36,C37) | 1500
Required diamter, m | SQRT(4*C38/3.14) | 43.713
Resulting weir length, m | 3.14*C39 | 137.2589
Resulting weirloading rate at average flow, m3/m /day | (C26)*1000/C40 | 167.5666
Weir loading rate in average flow from Table 5.8, m3/m /day | Enter | 185
Usage of double sided weir is needed or not | Enter | No
Choose a launder clear annular space from inner sidewall of clarifier, m | Enter | 0.2
Side water depth shall be to suit Table 5.8
In actual practice, the diamter and side water depths will be not less than the above values
Depending on the area and diameter, multiple number of these clarifiers may be designed