## Appendix-A6-1
Appendix A6-1
Illustrative Computation of Sludge weights and volumes from ASP
Raw sewage flow in MLD | Enter |  | 10
Raw sewage BOD in mg/l | Enter |  | 250
Raw sewage SS in mg/l | Enter |  | 400
Raw sewage VSS in percent | Enter |  | 60
Raw sewage ISS in percent |  | 100-D6 | 40
Secondary clarifier effluent BOD in mg/l | Enter |  | 10
Consider Primary Clarifier alone
BOD removal in percent | Enter |  | 30
Effluent BOD in mg/l |  | D4*(100-D10)/100 | 175
ISS removal in percent | Enter |  | 60
VSS removal in percent | Enter |  | 60
TSS removal in percent |  | 100*((D6*D12/100)+(D7*D13/100))/(D6+D7) | 60
VSS removed in kg / day |  | D3*D5*D6*D13/100/100 | 1440
ISS removed in Kg / day |  | D3*D5*D7*D12/100/100 | 960
TSS removed in Kg / day |  | SUM(D15:D16) | 2400
% solids in primary sludge | Enter |  | 4
Specific gravity of primary sludge | Enter |  | 1
Sludge removed in Kld |  | D17*100/D18/D19/1000 | 60
BOD removed in Kg / day |  | D3*D4*D10/100 | 750
Kg VSS / Kg BOD removed |  | D15/D21 | 1.92
Kg ISS / Kg BOD removed |  | D16/D21 | 1.28
Kg TSS / Kg BOD removed |  | D17/D21 | 3.2
ISS carry over in kg / day |  | (D3*D5*D7/100)-D16 | 640
Consider conventional secondary stage alone
Clarifier effluent BOD in mg/l | Enter |  | 10
Secondary clarifier VSS in percent | Enter |  | 85
Secondary clarifier ISS in percent |  | 100-D28 | 15
Aeration kd in per day | Enter |  | 0.06
Aeration Y | Enter |  | 0.5
Aeration SRT in days | Enter |  | 5
Kg VSS / Kg BOD removed, Y observed = Y/(1+ (kd)*( SRT)) |  | D31/(1+(D30)*(D32)) | 0.38462
BOD removed in kg / day |  | D3*(D11-D27) | 1650
Kg VSS removed per day |  | D33*D34 | 634.6154
SS removed in kg / day |  | D35*100/D28 | 746.6063
Inert sludge carry over in kg/day |  | (D3*D5*D7/100) | 1600
Kg TSS carried over per day |  | SUM(D36:D37) | 2346.6063
% solids in sludge |  | Enter | 0.75
Specific gravity |  | Enter | 1
Sludge removed in Kld |  | D38*100/D39/D40/1000 | 312.8808
Kg VSS / Kg BOD removed |  | D35/D34 | 0.38462
Kg TSS / Kg BOD removed |  | D38/D34 | 1.4222
Consider extended aeration alone
Clarifier effluent BOD in mg/l | Enter |  | 10
Aeration kd in per day | Enter |  | 0.06
Aeration Y | Enter |  | 0.5
Aeration SRT in days | Enter |  | 15
Kg VSS / Kg BOD removed, Y observed = Y/(1+ (kd)*( SRT)) |  | D47/(1+(D46)*(D48)) | 0.26316
BOD removed in kg / day |  | D3*(D4-D45) | 2400
Kg VSS removed per day |  | D49*D50 | 631.5789
Inert sludge carry over in kg/day |  | D3*D5*(D7)/100 | 1600
Kg TSS removed per day |  | SUM(D51:D52) | 2231.5789
% solids in sludge |  | Enter | 0.75
Specific gravity |  | Enter | 1
Sludge removed in Kld |  | D53*100/D54/D55/1000 | 297.5439
Kg VSS / Kg BOD removed |  | D51/D50 | 0.26316
Kg TSS / Kg BOD removed |  | D53/D50 | 0.92982
Rule of Thumb for Design Purposes for parameters as above.
For other parameters please rework in the M S excel
Kg Sludge / Kg BOD removed
Process | as VSS | as TSS
Primary alone | 1.92 | 3.2
Primary and secondary as conventional ASP | 0.86442 | 1.3111
Extended aeration ASP | 0.26316 | 0.92982