## K&C-Sewer
Pump Friction Loss and HP Calculations for K&C Valley-Terminal Gravity Sewer for 407 mld
Slope 1 in | 580 | Choose and enter | 800 | 1100 | 1500 | 1950
| 0.0017241 |  | 0.00125 | 0.00090909 | 0.00066667 | 0.00051282
| 0.032192 |  | 0.02706 | 0.022785 | 0.019271 | 0.016726
D in m | 1.4 | Choose and enter | 1.5 | 1.6 | 1.7 | 1.8
| 0.7 |  | 0.75 | 0.8 | 0.85 | 0.9
| 0.79875 |  | 0.83424 | 0.86885 | 0.90268 | 0.93578
| 0.849 |  | 0.849 | 0.849 | 0.849 | 0.849
Hazen C | 140 | Enter | 140 | 140 | 140 | 140
Velocity m/s | 3.0563 | Value | 2.6832 | 2.353 | 2.0677 | 1.8603
| 1.96 |  | 2.25 | 2.56 | 2.89 | 3.24
| 3.14 |  | 3.14 | 3.14 | 3.14 | 3.14
| 4 |  | 4 | 4 | 4 | 4
| 1.5386 |  | 1.7663 | 2.0096 | 2.2687 | 2.5434
Flow in lps | 4702.4274 | Value | 4739.2313 | 4728.6807 | 4690.8103 | 4731.5614
Flow in cum / sec | 4.7024 |  | 4.7392 | 4.7287 | 4.6908 | 4.7316
Flow in mld | 406.2897 |  | 409.4696 | 408.558 | 405.286 | 408.8069
Length in m | 4700 | Enter | 4700 | 4700 | 4700 | 4700
Friction head in m | 8.1034 | Value | 5.875 | 4.2727 | 3.1333 | 2.4103
Static head in m | 10 | Enter | 10 | 10 | 10 | 10
Losses in specials in m | 1.6207 | Enter | 1.175 | 0.85455 | 0.62667 | 0.48205
Total head for pump | 19.7241 | Value | 17.05 | 15.1273 | 13.76 | 12.8923
Efficiency | 0.65 | Enter | 0.65 | 0.65 | 0.65 | 0.65
HP of pump | 1902.5913 | Value | 1657.5158 | 1467.324 | 1324.0113 | 1251.2974
Kw of pump | 1419.3331 | Value | 1236.5068 | 1094.6237 | 987.7124 | 933.4678
Cost per Kl | 0.46113 |  | 0.39861 | 0.35366 | 0.32169 | 0.30141
Cost of PS in Rs. crores | 3.5483 |  | 3.0913 | 2.7366 | 2.4693 | 2.3337
Cost pf pipeline Rs. Crores | 16.45 |  | 17.39 | 17.86 | 18.33 | 18.8
Total cost Rs. Crores | 19.9983 |  | 20.4813 | 20.5966 | 20.7993 | 21.1337
Electrical p a Rs. Crores | 6.8383 |  | 5.9575 | 5.2739 | 4.7588 | 4.4974

## Summary of Sizes and Economics
K&C Valley-Economics of Pumping Main
Dia | V | Kw/100 | Capital | Elec P A
mm | m/s |  | Rs crores | Rs. Crores
1.4 | 3.0563 | 14.1933 | 19.9983 | 6.8383
1.5 | 2.6832 | 12.3651 | 20.4813 | 5.9575
1.6 | 2.353 | 10.9462 | 20.5966 | 5.2739
1.7 | 2.0677 | 9.8771 | 20.7993 | 4.7588
1.8 | 1.8603 | 9.3347 | 21.1337 | 4.4974
ISPS-MH-077
Dia | V | Kw/100 | Capital | Elec P A
mm | m/s |  | Rs crores | Rs. Crores
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!
ISPS-MH-052-021
Dia | V | Kw/100 | Capital | Elec P A
mm | m/s |  | Rs crores | Rs. Crores
0 | 3272275.4596 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
ISPS-MH-009
Dia | V | Kw/100 | Capital | Elec P A
mm | m/s |  | Rs crores | Rs. Crores
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF!

## Appendix-A3-6
Appendix A3-6
Hazen Williams Formula for Circular Sewers Flowing Under Pressure
Given diameter and slope, find velocity and flow rate
This is left blank for the designer to enter his design notes
This is left blank for the designer to enter his design notes
This is left blank for the designer to enter his design notes
diameter, mm | 300 | Enter by Designer
Slope 1 in | 210 | Enter by Designer
Hazen Willams C | 140 | Enter from Table 3-14
diamter power 0.63 | 36.3569 | POWER(B7,0.63)
diamter power 2.63 | 3272117.5704 | POWER(B7,2.63)
Slope power 0.54 | 0.055719 | POWER((1/B8),0.54)
Velocity m/s | 1.2952 | (4.567/1000)*B9*B10*B12
Flow rate cum / day | 7912.6182 | (3.1/10000)*B11*B12*B9
Flow rate in MLD | 7.9126 | B14/1000
Given flow rate and slope of sewer, find diameter and velocity
Discharge cum / day | 7913 | Enter by Designer
Slope 1 in | 210 | Enter by Designer
Slope power 0.54 | 0.055719 | POWER(1/B19,0.54)
Hazen Williams C | 140 | Enter from Table 3-14
diameter power 2.63 | 3272275.4596 | B18/(3.1/10000)/B20/B21
diameter, mm | 300.0055 | POWER(B22,(1/2.63))
diameter power 0.63 | 36.3573 | Power(B23,0.63)
velocity, m/s | 1.2952 | (4.567/1000)*B20*B21*B24