## Part-C-Table-5-1
Part-C-Table 5-1
Establishment Cost Calculation in Rs Lakhs for Illustrative Capacities of Sewer Systems
The numbers in the cells bound by columns B to J and rows from 5 to 26 are considered reasonable
The fraction of time charged is to utilize the services more effectively in other sectors in the remaining time
Length of sewers in km | 5 | 10 | 20 | 50 | 100 | 150 | 200 | 250 | 300 | monthly pay
Executive Engineer |  |  |  |  | 1 | 2 | 3 | 3 | 4 | 80000
Portion of time charged for Sewers |  |  |  |  | 1 | 0.75 | 0.75 | 1 | 1
Assistant Executive Engineer |  |  | 1 | 2 | 2 | 4 | 6 | 6 | 8 | 60000
Portion of time charged for Sewers |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
Assistant Engineer | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 40000
Portion of time charged for Sewers | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Junior Engineer | 2 | 2 | [7 empty] | 30000
Portion of time charged for Sewers | 1 | 1
IIT qualified plumber | 1 | 1 | 2 | 2 | 3 | 4 | 5 | 6 | 8 | 15000
semi-skilled labourers | 2 | 2 | 2 | 2 | 3 | 4 | 5 | 6 | 8 | 12000
unskilled labourers | 2 | 2 | 4 | 6 | 8 | 10 | 12 | 16 | 20 | 10000
watchman & security | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 10000
Office assistant | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15000
Office computer operator | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20000
Office driver | [5 empty] | 1 | 1 | 1 | 1 | 15000
tapal messenger | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10000
Monthly salary in Rs lakhs | 2.34 | 2.74 | 3.09 | 3.89 | 5.16 | 7.78 | 10.05 | 11.72 | 14.66
Leave salary allowances as % | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Administrative overheads as % | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Margin for emergencies at % | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Margin for retirement benefits | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Monthly salary in Rs lakhs | 3.276 | 3.836 | 4.326 | 5.446 | 7.224 | 10.892 | 14.07 | 16.408 | 20.524
Monthly salary, Rs Lakhs /km sewer | 0.6552 | 0.3836 | 0.2163 | 0.10892 | 0.07224 | 0.072613 | 0.07035 | 0.065632 | 0.068413

## Part-C-Table-5-2
Part-C-Table 5-2
Establishment Costs in Rs Lakhs Calculation for Illustrative Capacities of Sewage Pumping Stations (SPS)
The numbers in the cells bound by columns B to J and rows from 5 to 26 are considered reasonable
The fraction of time charged is to utilize the services more effectively in other sectors in the remaining time
Installed Kw of pump sets | 50 | 100 | 150 | 200 | 400 | 600 | 800 | 1000 | 1300 | monthly pay
Executive Engineer |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 80000
Portion of time charged for SPS |  |  |  |  | 0.25 | 0.25 | 0.5 | 0.5 | 1
Assistant Executive Engineer |  |  | 1 | 2 | 2 | 2 | 2 | 3 | 4 | 60000
Portion of time charged for SPS |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
Assistant Engineer | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 40000
Portion of time charged for SPS | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Junior Engineer | 2 | 2 | [7 empty] | 30000
Portion of time charged for SPS | 1 | 1
IIT qualified plumber | 1 | 2 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 15000
semi-skilled labourers | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 12000
unskilled labourers | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4 | 4 | 10000
watchman & security | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 10000
Office assistant | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15000
Office computer operator | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20000
Office driver | [5 empty] | 1 | 1 | 1 | 1 | 15000
tapal messenger | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10000
Monthly salary in Rs lakhs | 2.34 | 2.89 | 3.19 | 4.09 | 4.49 | 4.64 | 4.84 | 5.44 | 6.44
Leave salary allowances as % | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Administrative overheads as % | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Margin for emergencies at % | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Retirement benefits | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Monthly salary in Rs lakhs | 3.276 | 4.046 | 4.466 | 5.726 | 6.286 | 6.496 | 6.776 | 7.616 | 9.016
Monthly salary in Rs Lakhs per 1000Kw | 65.52 | 40.46 | 29.7733 | 28.63 | 15.715 | 10.8267 | 8.47 | 7.616 | 6.9354

## Part-C-Table-5-4
Part-C-Table 5-4
Operating capacity of STP in MLD | [6 empty] | Enter | 15
Cost of electricity in Rs per kwhr | [6 empty] | Enter | 6
Illustrative costing of electricity charges for a 15 MLD capacity with DAF-Nitrification-Denitrification STP
| Kw Rating | Efficiency | Load factor | working | PF at full load | Operating Load in KW | Running Hours | KWH
Raw Sewage pump for wet weather | 90 | 0.85 | 0.85 | 1 | 0.88 | 76.5 | 8 | 612
Raw Sewage pump for dry weather | 55 | 0.85 | 0.85 | 1 | 0.87 | 46.75 | 24 | 1122
Mechanical coarse bar screen | 1.1 | 0.77 | 0.85 | 1 | 0.81 | 0.935 | 24 | 22.44
Mechanical fine bar screen | 1.1 | 0.77 | 0.85 | 1 | 0.81 | 0.935 | 24 | 22.44
Conveyor for coarse screenings | 1.5 | 0.75 | 0.85 | 1 | 0.81 | 1.275 | 24 | 30.6
Grit Remover | 0.75 | 0.75 | 0.85 | 2 | 0.77 | 1.275 | 24 | 30.6
Classifier for grit chamber | 1.5 | 0.75 | 0.85 | 2 | 0.77 | 2.55 | 24 | 61.2
Organic Pump for Grit chamber | 0.75 | 0.75 | 0.85 | 2 | 0.77 | 1.275 | 24 | 30.6
Air Compressor for DAF | 5.5 | 0.85 | 0.85 | 1 | 0.82 | 4.675 | 24 | 112.2
Dosing Pump for DAF | 2.2 | 0.7 | 0.85 | 4 | 0.9 | 7.48 | 24 | 179.52
Agitator for DAF dosing tank | 3.7 | 0.75 | 0.85 | 8 |  | 25.16 | 24 | 603.84
Pump for DAF (HPP) | 37 | 0.92 | 0.85 | 1 | 0.9 | 31.45 | 24 | 754.8
DAF Unit | 1.5 | 0.75 | 0.85 | 2 | 0.81 | 2.55 | 24 | 61.2
DAF Clarified Water Transfer Pump | 30 | 0.85 | 0.85 | 2 | 0.83 | 51 | 24 | 1224
Agitator for pH correction tank | 0.37 | 0.77 | 0.85 | 1 | 0.81 | 0.3145 | 20 | 6.29
Primary Clarifiers | 1.5 | 0.75 | 0.85 | 2 | 0.77 | 2.55 | 24 | 61.2
Primary sludge pumpsets | 10 | 0.5 | 0.85 | 2 | 0.77 | 17 | 6 | 102
Agitator for Nutrient Dosing Tank | 11 | 0.8 | 0.85 | 2 | 0.83 | 18.7 | 24 | 448.8
Agitator for anoxic tank | 3.7 | 0.8 | 0.85 | 2 | 0.83 | 6.29 | 24 | 150.96
Internal return pump | 37 | 0.95 | 0.85 | 2 | 0.88 | 62.9 | 24 | 1509.6
Air Compressor for aeration tank | 110 | 0.95 | 0.85 | 4 | 0.88 | 374 | 24 | 8976
Return and excess sludge pump | 37 | 0.92 | 0.85 | 2 | 0.9 | 62.9 | 24 | 1509.6
Agitator for ferric chloride dosing tank | 1.1 | 0.77 | 0.85 | 1 | 0.81 | 0.935 | 24 | 22.44
Secondary Clarifiers | 1.5 | 0.75 | 0.85 | 2 | 0.77 | 2.55 | 24 | 61.2
Thickner mechanism | 1.1 | 0.75 | 0.85 | 2 | 0.77 | 1.87 | 24 | 44.88
Dilution Water Pumps | 20 | 0.9 | 0.8 | 2 | 0.9 | 32 | 24 | 768
Digester feed pumps | 30 | 0.5 | 0.85 | 2 | 0.9 | 51 | 24 | 1224
Digester mixers | 60 | 0.85 | 0.85 | 1 | 0.87 | 51 | 24 | 1224
Centrifuge feed pump | 0.75 | 0.7 | 0.85 | 2 | 0.72 | 1.275 | 24 | 30.6
Poly dosing pump for centrifuge | 0.37 | 0.75 | 0.85 | 1 | 0.77 | 0.3145 | 24 | 7.548
Centrifuge | 7.5 | 0.75 | 0.85 | 1 | 0.83 | 6.375 | 24 | 153
Filtrate transfer pumps | 10 | 0.85 | 0.85 | 2 | 0.83 | 17 | 24 | 408
Air Compressor for Instruments | 7.5 | 0.83 | 0.85 | 1 | 0.84 | 6.375 | 20 | 127.5
DMF feed pump | 75 | 0.938 | 0.85 | 2 | 0.87 | 127.5 | 20 | 2550
DMF backwash pump | 30 | 0.92 | 0.85 | 2 | 0.9 | 51 | 4 | 204
DMF air blower | 11 | 0.884 | 0.85 | 2 | 0.87 | 18.7 | 4 | 74.8
Single Phase Receptacles & Exhaust | 22.5 | 0.9 | 0.8 | 2 | 0.9 | 36 | 24 | 864
Treated water transfer pump | 45 | 0.925 | 0.85 | 1 | 0.9 | 38.25 | 20 | 765
Lighting Load | 55 | 0.9 | 0.8 | 1 | 0.9 | 44 | 15 | 660
Total upto end of tertiary filtration | [5 empty] | 1284.609 |  | 26820.858
Electrical energy in kwhr per Kiloliter of sewage upto end of secondary treatment | [7 empty] | 18231.998
Electrical energy in kwhr per Kiloliter of sewage for tertiary filtration | [7 empty] | 5653.3
Electrical cost per kiloliter of sewage upto end of secondary treatment | [7 empty] | 7.2928
Electrical cost per kiloliter of sewage for tertiary filtration | [7 empty] | 2.2613

## Part-C-Table-5-3
Part-C-Table 5-3
Establishment Cost in Rs Lakhs Calculation for Illustrative Capacities of Mechanized Sewage Treatment Plants (STPs)
The numbers in the cells bound by columns B to J and rows from 5 to 29 are considered reasonable
The fraction of time charged is to utilize the services more effectively in other sectors in the remaining time
Operating MLD of STP | 5 | 10 | 20 | 60 | 100 | 150 | 200 | 250 | 300 | monthly pay
Executive Engineer |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 80000
Portion of time charged for STP |  |  |  |  | 0.25 | 0.5 | 0.75 | 1 | 1
Assistant Executive Engineer |  |  | 1 | 1 | 2 | 2 | 3 | 3 | 3 | 60000
Portion of time charged for STP |  |  | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
Assistant Engineer |  |  | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 40000
Portion of time charged for STP |  |  | 0.5 | 1 | 0.25 | 0.5 | 0.75 | 1 | 1
Junior Engineer | 2 | 2 | [7 empty] | 30000
Portion of time charged for STP | 1 | 1
Diploma qualified electrician |  |  | 1 | 1 | 3 | 3 | 3 | 3 | 3 | 20000
IIT qualified electrician | 1 | 2 | 2 | 2 | [5 empty] | 15000
IIT qualified plumber | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 15000
semi-skilled labourers | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 12000
unskilled labourers | 2 | 2 | 2 | 4 | 4 | 6 | 6 | 9 | 9 | 10000
watchman & security | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 10000
Office assistant | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15000
Office computer operator | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20000
Office driver | [5 empty] | 1 | 1 | 1 | 1 | 15000
Chemist | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 25000
microbiologist | [7 empty] | 1 | 1 | 25000
lab assistant | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 12000
tapal messenger | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10000
Monthly salary in Rs lakhs | 2.34 | 2.61 | 3.11 | 4.33 | 4.48 | 5.38 | 6.8 | 7.85 | 7.97
Leave salary allowances as % | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Administrative overheads as % | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Margin for emergencies at % | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Retirement benefits | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Monthly salary in Rs lakhs | 3.276 | 3.654 | 4.354 | 6.062 | 6.272 | 7.532 | 9.52 | 10.99 | 11.158
Monthly salary in Rs Lakhs per MLD | 0.6552 | 0.3654 | 0.2177 | 0.10103 | 0.06272 | 0.050213 | 0.0476 | 0.04396 | 0.037193